## Slide 1
DOE Full Model Analysis (820 Parameters)
Design of Experiments Analysis

## Slide 2
Model Fit Diagram

## Slide 3
Model Equation
Interface_Temp = β₀ + Σ(β_i × Factor_i) + ε
Where:
• β₀ = Intercept
• β_i = Parameter coefficients
• Factor_i = Design factors (Transceiver, Fan Speed, Rack Unit)
• ε = Random error term
Full Model: 820 parameters | Model Type: Multiple Linear Regression | Response: Interface_Temp

## Slide 4
Model Comparison: Full vs Reduced
Metric | Full Model | Reduced Model | Difference
Parameters | 820 | 451 | -369 (-45%)
R² | 0.3897 | 0.3852 | -0.0045 (-1.1%)
Adjusted R² | 0.3830 | 0.3816 | -0.0014
MSE | 1.7437 | 1.7460 | +0.0023 (+0.1%)
F-Statistic | 58.42 | 108.36 | +49.94
p-value | <0.001 | <0.001 | N/A

## Slide 5
ANOVA Table (Type I - Sequential)
Unnamed: 0 | df | sum_sq | mean_sq | F | PR(>F)
Transceiver_Manufacturer | 9 | 3416.87 | 379.652 | 217.728 | 0
Rack_Unit | 40 | 420.47 | 10.5118 | 6.02843 | 5.81e-30
Fan_Speed_Range | 1 | 1.65064 | 1.65064 | 0.94663 | 0.330611
Transceiver_Manufacturer*Rack_Unit | 360 | 4773 | 13.2583 | 7.60358 | 1.51e-294
Transceiver_Manufacturer*Fan_Speed_Range | 9 | 49.5824 | 5.50916 | 3.15947 | 8.19e-04
Rack_Unit*Fan_Speed_Range | 40 | 81.5171 | 2.03793 | 1.16874 | 0.215706
Transceiver_Manufacturer*Rack_Unit | 360 | 744.722 | 2.06867 | 1.18637 | 0.0101534
Residual | 7382 | 12872 | 1.7437 | nan | nan

## Slide 6
Parameter Table (Sorted by P-value, Low to High)
Unnamed: 0 | Coefficient | Std Error | t-value | p-value | Lower CI | Upper CI | Significance
Intercept | 65.0873 | 0.0800917 | 812.66 | 0 | 64.9303 | 65.2443 | Significant
Transceiver_Manufacturer*Rack_Unit[NON-JNPR,5] | 65.1494 | 1.41431 | 46.0644 | 0 | 62.3769 | 67.9218 | Significant
Transceiver_Manufacturer[Finisar] | -1.33263 | 0.117195 | -11.3711 | 0 | -1.56237 | -1.1029 | Significant
Transceiver_Manufacturer[Accelight] | -1.32759 | 0.133406 | -9.95153 | 0 | -1.5891 | -1.06608 | Significant
Transceiver_Manufacturer[NON-JNPR] | -2.83028 | 0.473603 | -5.97606 | 0 | -3.75868 | -1.90188 | Significant
Rack_Unit[6] | -1.24505 | 0.26672 | -4.66801 | 3.00e-06 | -1.7679 | -0.722203 | Significant
Transceiver_Manufacturer[O-NET] | -2.49321 | 0.544998 | -4.57471 | 5.00e-06 | -3.56156 | -1.42486 | Significant
Transceiver_Manufacturer[Hisense] | -1.72336 | 0.406196 | -4.24268 | 2.20e-05 | -2.51962 | -0.927099 | Significant
Rack_Unit[7] | -0.803411 | 0.237452 | -3.38346 | 7.20e-04 | -1.26889 | -0.337936 | Significant
Rack_Unit[23] | -2.21613 | 0.665311 | -3.33096 | 8.70e-04 | -3.52033 | -0.911928 | Significant
Rack_Unit[24] | -2.49384 | 0.766877 | -3.25195 | 0.001151 | -3.99714 | -0.990544 | Significant

## Slide 7
Leverage Plot 1

## Slide 8
Leverage Plot 2

## Slide 9
Leverage Plot 3

## Slide 10
Leverage Plot 4

## Slide 11
Leverage Plot 5

## Slide 12
Leverage Plot 6

## Slide 13
Leverage Plot 7

## Slide 14
Leverage Plot 8

## Slide 15
Leverage Plot 9

## Slide 16
Leverage Plot 10

## Slide 17
Leverage Plot 11

## Slide 18
Leverage Plot 12

## Slide 19
Leverage Plot 13

## Slide 20
Leverage Plot 14

## Slide 21
Leverage Plot 15

## Slide 22
Leverage Plot 16

## Slide 23
Leverage Plot 17

## Slide 24
Leverage Plot 18

## Slide 25
Leverage Plot 19

## Slide 26
Leverage Plot 20

## Slide 27
Leverage Plot 21

## Slide 28
Leverage Plot 22

## Slide 29
Leverage Plot 23

## Slide 30
Leverage Plot 24

## Slide 31
Leverage Plot 25

## Slide 32
Leverage Plot 26

## Slide 33
Leverage Plot 27

## Slide 34
Leverage Plot 28

## Slide 35
Leverage Plot 29

## Slide 36
Leverage Plot 30

## Slide 37
Leverage Plot 31

## Slide 38
Leverage Plot 32

## Slide 39
Leverage Plot 33

## Slide 40
Leverage Plot 34

## Slide 41
Leverage Plot 35

## Slide 42
Leverage Plot 36

## Slide 43
Leverage Plot 37

## Slide 44
Leverage Plot 38

## Slide 45
Leverage Plot 39

## Slide 46
Leverage Plot 40

## Slide 47
Leverage Plot 41

## Slide 48
Leverage Plot 42

## Slide 49
Leverage Plot 43

## Slide 50
Leverage Plot 44

## Slide 51
Leverage Plot 45

## Slide 52
Leverage Plot 46

## Slide 53
Leverage Plot 47

## Slide 54
Leverage Plot 48

## Slide 55
Leverage Plot 49

## Slide 56
Leverage Plot 50

## Slide 57
Leverage Plot 51